## question
Any | Designation (ClassAny) an allen relevanten Unterstromkreisen pflegn? -- untersch Defaultwert
preferences | VoltageFactorCMax
VoltageFactorCMin und Max --> derzeit nur 1 Merkmale aber untersch. Default für LV und MV, moment nicht adäquat im Modell enthalten
Circuit | SystemConfiguration
derzeit nur 1 Merkmal aber untersch. Default für StLoad und circuit, moment nicht adäquat im Modell enthalten
ClassInfeed | NominalApparentPower
Defaultwert und Range sind erfunden--> Zulieferung durch Kunden nötig
ClassConsumer
cosPhi--> derzeit nur 1 Merkmal aber untersch. Quellen des aktuellen Wertes für StLoad (eingabe) und rest (Kalkulation)
Allgemein:
in aktueller Datei (und cistic Overview) Rules für alle kalkulierten Werte hinterlegen
Dokumentation der Quelle des aktuellen Wertes in Overview Cistic überabeiten, --> kann unter Rule hinterlegt sein (entweder Fornel oder Dbvalue)

## Revision
Date | Description | Version | Author | Status Implementation | Status Product Knowledge | Change Valid From in ERP | Knowledge Base Version CRM
2016-04-15 | Document created | 0.1 | K.Heylen | not implemented
2016-04-22 | Formula "links" added | 0.6 | M.Berbig | not implemented

## Taxonomy
Class | SuperClass | Label |  | Comment
|  | EN | DE | EN | DE
General | KnowledgeBase
ElectricalDesignDocument | General
Impedance | General
Circuit | General
DataPoint | General
Infeed | Impedance
Connection | Impedance
Consumer | Impedance
Metering | DataPoint
Switch | DataPoint
Transformer | Infeed
Cable | Connection
CableLV | Cable
CableMV | Cable
StaticLoad | Consumer
BreakerLV | Switch
BreakerMV | Switch

## KBInstances
ObjectName | Class | Type | Parts | Label |  | Comment
|  |  |  | EN | DE | EN | DE
Transformer | Transformer | DesignStencil
MSnet | Infeed | DesignStencil
Generator | Infeed | DesignStencil
CableLV | CableLV | DesignStencil
CableMV | CableMV | DesignStencil
Busway | Connection | DesignStencil
StaticLoad | StaticLoad | DesignStencil
Motor | Consumer | DesignStencil
Fuse | BreakerLV | DesignStencil
MCB | BreakerLV | DesignStencil
RCD | Contactor | DesignStencil
ElectricalDesignDocument | ElectricalDesignDocument | DesignDocumentType
TransformerCircuitLV | Circuit | DesignCompound | Transformer, CableLV, BreakerLV

## ClassGeneral
Class name | General | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
General
| Designation | char | x | [9 empty] | Designation
[5 empty] | x | name | [6 empty] | Name

## ClassElectricalDesignDocument
Class name | ElectricalDesignDocument | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
NetworkParameter | [12 empty] | Network parameter
| AmbientTemperature | decimal | x |  |  |  | 30 | 60 |  |  |  |  | Ambient temperature [°C]
[5 empty] | x | 40
| VoltageFactorCMax | decimal | x |  |  |  | 1.1 | 1.1 |  |  |  |  | Voltage factor c max
[5 empty] | x | 1.1
| VoltageFactorCMinMV | decimal | x |  |  |  | 1 | 1 |  |  |  |  | Voltage factor c minMV
[5 empty] | x | 1
| VoltageFactorCMinLV | decimal | x |  |  |  | 0.95 | 0.95 |  |  |  |  | Voltage factor c minLV
[5 empty] | x | 0.95
| RelationR1_X1min | decimal | x |  |  |  | 0.2 | 0.2 |  |  |  |  | Relation R1/X1 min
[5 empty] | x | 0.2
| NominalVoltageMV | decimal | x |  |  |  | 5000 | 40000 |  |  |  |  | Nominal voltage medium voltage [V]
[5 empty] | x | 20000
| NominalVoltageLV | decimal | x |  |  |  | 200 | 1000 |  |  |  |  | Nominal voltage low voltage [V]
[5 empty] | x | 400
| MaxShortCircuitPower | decimal | x |  |  |  | 10 | 1000 |  |  |  |  | Max. short-circuit power [MVA]
[5 empty] | x | 250
| MinShortCircuitPower | decimal | x |  |  |  | 10 | 0,9*MaxShortCircuitPower |  |  |  |  | Min. short-circuit power [MVA]
[5 empty] | x | 100
| RefPtVoltDropCalculation | choice | x | x | [8 empty] | Reference point of voltage drop calculation
[5 empty] | x | TransformerPrimTerminals | [6 empty] | Transformer-primary terminals
[6 empty] | TransformerSecTerminals | [6 empty] | Transformer-secondary terminals
RequirementParameter | [12 empty] | Requirement parameter
| CondTempLVCable | decimal | x |  |  |  | 0 | 100 |  |  |  |  | θΔu [°C]
[5 empty] | x | 50
| CondTempLVCableBeginShortCircuit | decimal | x |  |  |  | 20 | 20 |  |  |  |  | θIkmax [°C]
[5 empty] | x | 20
| CondTempLVCableDiscon | decimal | x |  |  |  | 0 | 100 |  |  |  |  | θIkmin [°C]
[5 empty] | x | 70
ResultParameter | [12 empty] | Result parameter
| R1maxMV | decimal | x | [6 empty] | 00-01 |  |  | R1max [mΩ]
| X1maxMV | decimal | x | [6 empty] | 00-02 |  |  | X1max [mΩ]
| Z1maxMV | decimal | x | [6 empty] | 00-03 |  |  | Z1max [mΩ]
| R1minMV | decimal | x | [6 empty] | 00-04 |  |  | R1min [mΩ]
| X1minMV | decimal | x | [6 empty] | 00-05 |  |  | X1min [mΩ]
| Z1minMV | decimal | x | [6 empty] | 00-06 |  |  | Z1min [mΩ]

## ClassImpedance
Class name | Impedance | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | ENShortText | DE
RequirementParameter | [12 empty] | Requirement parameter
| operatingCurrent | decimal | x |  | C |  | C | C |  | 01-01 |  |  | Operating / load current [A]
| loadCurrent | decimal | x |  | C |  | C | C |  | 01-02 |  |  | Operating / load current [A]
| RelativeVoltageDrop | decimal | x |  | C |  | 0 | 100 |  | 01-03 |  |  | Δu [%]
| RelativeCumVoltageDrop | decimal | x |  | C |  | 0 | 100 |  | 01-04 |  |  | ∑Δu [%]
ResultParameter | [12 empty] | Result parameter
| R1max | decimal | x | [6 empty] | 01-05 |  |  | R1max [mΩ]
| X1max | decimal | x | [6 empty] | 01-06 |  |  | X1max [mΩ]
| Z1max | decimal | x | [6 empty] | 01-07 |  |  | Z1max [mΩ]
| R0max | decimal | x | [6 empty] | 01-08 |  |  | R0max [mΩ]
| X0max | decimal | x | [6 empty] | 01-09 |  |  | X0max [mΩ]
| Z0max | decimal | x | [6 empty] | 01-10 |  |  | Z0max [mΩ]
| R1min | decimal | x | [6 empty] | 01-11 |  |  | R1min [mΩ]
| X1min | decimal | x | [6 empty] | 01-12 |  |  | X1min [mΩ]
| Z1min | decimal | x | [6 empty] | 01-13 |  |  | Z1min [mΩ]
| R0min | decimal | x | [6 empty] | 01-14 |  |  | R0min [mΩ]
| X0min | decimal | x | [6 empty] | 01-15 |  |  | X0min [mΩ]
| Z0min | decimal | x | [6 empty] | 01-16 |  |  | Z0min [mΩ]
| sumAbsVoltageDrop | decimal | x | [6 empty] | 01-17 |  |  | ΣΔU [V]
| RatedEffectivePower | decimal | x | [6 empty] | 01-18 |  |  | P [kW]
| ReactivePower | decimal | x | [6 empty] | 01-19 |  |  | Q [kvar]
| RatedPower | decimal | x | [6 empty] | 01-20 |  |  | S [kVA]
RequirementAndResultParameter | [12 empty] | Requirement and Result parameter
| InTrafo | decimal |  |  | C |  | 0 | C |  | to be defined |  |  | Nominal current [A]

## ClassCircuit
Class name | Circuit | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
NetworkParameter | [12 empty] | Network parameter
| SystemConfiguration | choice | x | x | [8 empty] | System configuration
[6 empty] | TN_S | [6 empty] | TN-S
[5 empty] | x | TN_C | [6 empty] | TN-C
[6 empty] | IT | [6 empty] | IT
[6 empty] | TT | [6 empty] | TT
RequirementParameter | [12 empty] | Requirement parameter
| SimultaneityFactor | decimal | x |  |  |  | 0 | 1 |  |  |  |  | Simultaneity factor
[5 empty] | x | 1

## ClassDataPoint
Class name | DataPoint | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
ResultParameter | [12 empty] | Result parameter
| Ik3max | decimal | x | [6 empty] | 02-01 |  |  | Ik3max [kA]
| Ik1maxph_n | decimal | x | [6 empty] | 02-02 |  |  | Ik1maxph_n [kA]
| Ik1maxph_pe | decimal | x | [6 empty] | 02-03 |  |  | Ik1maxph_pe [kA]
| maxAsymShortCircuitCurrent | decimal | x | [6 empty] | 02-04 |  |  | Ipk [kA]
| Ik3min | decimal | x | [6 empty] | 02-05 |  |  | Ik3min [kA]
| Ik2min | decimal | x | [6 empty] | 02-06 |  |  | Ik2min [kA]
| Ik1minph_n | decimal | x | [6 empty] | 02-07 |  |  | Ik1minph_n [kA]
| Ik1minph_pe | decimal | x | [6 empty] | 02-08 |  |  | Ik1minph_pe [kA]
| phaseAngleIk3max | decimal | x | [6 empty] | 02-09 |  |  | φ3_max [°]
| phaseAngleIk1maxph_n | decimal | x | [6 empty] | 02-10 |  |  | φ1ph_n_max [°]
| phaseAngleIk1maxph_pe | decimal | x | [6 empty] | 02-11 |  |  | φ1ph_pe_max [°]
| phaseAngleIk3min | decimal | x | [6 empty] | 02-12 |  |  | φ3_min [°]
| phaseAngleIk2min | decimal | x | [6 empty] | 02-13 |  |  | φ2_min [°]
| phaseAngleIk1minph_n | decimal | x | [6 empty] | 02-14 |  |  | φ1ph_n_min [°]
| phaseAngleIk1minph_pe | decimal | x | [6 empty] | 02-15 |  |  | φ1ph_pe_min [°]
| Ik1max_F1 | decimal | x | [6 empty] | 02-16 |  |  | Ik1max(F1) [A]
| Ik3max_F1 | decimal | x | [6 empty] | 02-17 |  |  | Ik3max(F1) [A]
| Ik2min_F2 | decimal | x | [6 empty] | 02-18 |  |  | Ik2min(F2) [A]
| Ik3max_F3 | decimal | x | [6 empty] | 02-19 |  |  | Ik3max(F3) [A]
| Ik2min_F3 | decimal | x | [6 empty] | 02-20 |  |  | Ik2min(F3) [A]
| Ik1min_F3 | decimal | x | [6 empty] | 02-21 |  |  | Ik1min(F3) [A]
| Ik2min_F4 | decimal | x | [6 empty] | 02-22 |  |  | Ik2min(F4) [A]
| Ik1min_F4 | decimal | x | [6 empty] | 02-23 |  |  | Ik1min(F4) [A]
| Ikmin | decimal | x | [6 empty] | 02-24 |  |  | Ikmin [A]
| Ikmax | decimal | x | [6 empty] | 02-25 |  |  | Ikmax [A]
| totalActiveCurrent | decimal | x | [6 empty] | 02-26 |  |  | Igw [A]
| totalReactiveCurrent | decimal | x | [6 empty] | 02-27 |  |  | Igb [A]
| totalApparantCurrent | decimal | x | [6 empty] | 02-28 |  |  | Igs [A]
| activeLoadCurrent | decimal | x | [6 empty] | 02-29 |  |  | Ibw [A]
| reactiveLoadCurrent | decimal | x | [6 empty] | 02-30 |  |  | Ibb [A]

## ClassInfeed
Class name | Infeed | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
RequirementParameter | [12 empty] | Requirement parameter
| NominalApparentPower | decimal | x |  |  |  | 50 | 8000 |  |  |  |  | Nominal (apparent) power [kVA]
[5 empty] | x | 150 | [6 empty] | Result parameter
ResultParameter | Ibem | decimal | x | [6 empty] | 03-01 |  |  | Ibem [A]

## ClassConnection
Class name | Connection | [11 empty] | Localization |  | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE | EN | DE
RequirementParameter | [12 empty] | Requirement parameter
| AllowedLoadCapacity | decimal | x |  | C |  | C | C |  | To be defined |  |  | Allowed load capacity [A] |  | Nominal (apparent) power [kVA]
| Material | choice | x | x | [8 empty] | Material |  | Ibem [A]
[5 empty] | x | Cu | [6 empty] | Cu
| Length | decimal | x |  |  |  | 0.1 | 10000 |  |  |  |  | Length [m]
| CrossSectionPhaseConductor | decimal | x | [9 empty] | Cross section of phase conductor [mm2]
[5 empty] | x | 1.5 | [6 empty] | Basic data
BasicData
| conResPhaseCondPerUnitLength20Degr | decimal | x | [6 empty] | DBvalue |  |  | r1 [mΩ/m]
| conReactPhaseCondPerUnitLength | decimal | x | [6 empty] | DBvalue |  |  | x1 [mΩ/m]
| currentCarryingCapacity | decimal | x | [6 empty] | To be defined |  |  | Iz [A]

## ClassCableMV
Class name | CableMV | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
ResultParameter | [12 empty] | Result parameter
| R1maxMV_Cable | decimal | x | [6 empty] | 04-01 |  |  | R1max [mΩ]
| X1maxMV_Cable | decimal | x | [6 empty] | 04-02 |  |  | X1max [mΩ]
| R0maxMV_Cable | decimal | x | [6 empty] | 04-03 |  |  | R0max [mΩ]
| X0maxMV_Cable | decimal | x | [6 empty] | 04-04 |  |  | X0max [mΩ]
| R1minMV_Cable | decimal | x | [6 empty] | 04-05 |  |  | R1min [mΩ]
| X1minMV_Cable | decimal | x | [6 empty] | 04-06 |  |  | X1min [mΩ]
| R0minMV_Cable | decimal | x | [6 empty] | 04-07 |  |  | R0min [mΩ]
| X0minMV_Cable | decimal | x | [6 empty] | 04-08 |  |  | X0min [mΩ]
BasicData | [12 empty] | Basic data
| r0 | decimal | x | [6 empty] | DBvalue |  |  | r0 [mΩ/m]
| x0 | decimal | x | [6 empty] | DBvalue |  |  | x0 [mΩ/m]

## ClassCableLV
Class name | CableLV | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
RequirementParameter | [12 empty] | Requirement parameter
| InstallationType | choice | x | x | [8 empty] | Installation type
[6 empty] | A2 | [6 empty] | A2
[6 empty] | B1 | [6 empty] | B1
[6 empty] | B2 | [6 empty] | B2
[5 empty] | x | C | [6 empty] | C
[6 empty] | D1 | [6 empty] | D1
[6 empty] | D2 | [6 empty] | D2
[6 empty] | E | [6 empty] | E
| PermisVoltageDropPerSection | decimal | x |  |  |  | 0 | 20 |  |  |  |  | Permissable voltage drop / section [%]
[5 empty] | x | 4
| NumberRuns | decimal | x |  |  |  | 1 | 20 |  |  |  |  | Number of runs
[5 empty] | x | 1
| CrossSectionNConductor | decimal | x |  |  |  | 1.5 | 630 |  |  |  |  | Cross section of N conductor [mm2]
[5 empty] | x | 1.5
| CrossSectionPEConductor | decimal | x |  |  |  | 1.5 | 630 |  |  |  |  | Cross section of PE conductor [mm2]
[5 empty] | x | 1.5
| α | decimal | x
[6 empty] | Al | 0,00403 | [5 empty] | α [1/°C]
[6 empty] | Cu | 0,00393 | [5 empty] | α [1/°C]
ResultParameter | [12 empty] | Result parameter
| R1DeltaU | decimal | x | [6 empty] | 05-14 |  |  | R1ΔU [mΩ]
| X1DeltaU | decimal | x | [6 empty] | 05-15 |  |  | X1ΔU [mΩ]
| R0DeltaU | decimal | x | [6 empty] | 05-16 |  |  | R0ΔU [mΩ]
| X0DeltaU | decimal | x | [6 empty] | 05-17 |  |  | X0ΔU [mΩ]
| R1maxLV_Cable | decimal | x | [6 empty] | 05-01 |  |  | R1max [mΩ]
| X1maxLV_Cable | decimal | x | [6 empty] | 05-02 |  |  | X1max [mΩ]
| R0maxLV_Cable | decimal | x | [6 empty] | 05-03 |  |  | R0max [mΩ]
| X0maxLV_Cable | decimal | x | [6 empty] | 05-04 |  |  | X0max [mΩ]
| R1minLV_Cable | decimal | x | [6 empty] | 05-05 |  |  | R1min [mΩ]
| X1minLV_Cable | decimal | x | [6 empty] | 05-06 |  |  | X1min [mΩ]
| R0ph-nminLV_Cable | decimal | x | [6 empty] | 05-07 |  |  | R0ph-nmin [mΩ]
| R0ph-pe(n)minLV_Cable | decimal | x | [6 empty] | 05-08 |  |  | R0ph-pe(n)min [mΩ]
| X0ph-nminLV_Cable | decimal | x | [6 empty] | 05-09 |  |  | X0ph-nmin [mΩ]
| X0ph-pe(n)minLV_Cable | decimal | x | [6 empty] | 05-10 |  |  | X0ph-pe(n)min [mΩ]
| IbemInfeedCable | decimal | x | [6 empty] | 05-11 |  |  | Ibem infeed cable [A]
| IbemLVCable | decimal | x | [6 empty] | 05-12 |  |  | Ibem cable [A]
| absVoltageDropCable | decimal | x | [6 empty] | 05-13 |  |  | ΔU [V]
BasicData | [12 empty] | Basic data
| r0ph_n | decimal | x | [6 empty] | Dbvalue |  |  | r0ph-n [mΩ/m]
| r0ph_pe_n | decimal | x | [6 empty] | Dbvalue |  |  | r0ph-pe(n) [mΩ/m]
| x0ph_n | decimal | x | [6 empty] | Dbvalue |  |  | x0ph-n [mΩ/m]
| x0ph_pe_n | decimal | x | [6 empty] | Dbvalue |  |  | x0ph-pe(n) [mΩ/m]

## ClassConsumer
Class name | Consumer | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
RequirementParameter | [12 empty] | Requirement parameter
| cosPhi | decimal | x |  |  |  | 0.1 | 1 |  |  |  |  | cos φ
[5 empty] | x | 0.8
| Capacity_LoadFactor | decimal | x |  |  |  | 0 | 1 |  |  |  |  | Capacity factor / load factor
[5 empty] | x | 1
ResultParameter | [12 empty] | Result parameter
| PhaseAngleIn | decimal | x | [6 empty] | 06-01 |  |  | phase angle In [°]

## ClassSwitch
Class name | Contactor | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
RequirementAndResultParameter | [12 empty] | Requirement and Result parameter
| InContactor | decimal | x |  | C |  | 0.1 | 8000 |  | to be defined |  |  | Nominal current In [A]
ResultParameter | [12 empty] | Result parameter
| Ibem | decimal | x | [6 empty] | 07-01 |  |  | Ibem [A]
| Icu | decimal | x | [6 empty] | 07-02 |  |  | Icu [kA]
| Icm | decimal | x | [6 empty] | 07-03 |  |  | Icm [kA]
| Ikmax | decimal | x | [6 empty] | 07-04 |  |  | Ikmax [kA]
| Ikmin | decimal | x | [6 empty] | 07-05 |  |  | Ikmin [kA]

## ClassLVBreaker
Class name | LVBreaker | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
RequirementParameter | [12 empty] | Requirement parameter
| SwitchgearType | choice | x | x | [8 empty] | Type of switchgear low voltage
[6 empty] | none | [6 empty] | none
[5 empty] | x | Circuit-breaker | [6 empty] | Circuit-breaker
| fcm | decimal | x |  | C |  |  |  |  | 11-01 |  |  | fcm

## ClassMVBreaker
Class name | MVBreaker | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
RequirementParameter | [12 empty] | Requirement parameter
| SwitchgearType | choice | x | x | [8 empty] | Type of switchgear medium voltage
[5 empty] | x | Circuit-breaker | [6 empty] | Circuit-breaker

## ClassMCB
Class name | MCB | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
ResultParameter | [12 empty] | Result parameter
| Icn | decimal | x | [6 empty] | 08-01 |  |  | Icn [kA]

## ClassTrafo
Class name | Transformer | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
RequirementParameter | [12 empty] | Requirement parameter
| RatedShortCircuitVoltage | choice | x | x | [8 empty] | Rated short-circuit voltage
[5 empty] | x | 4
6
| ShortCircuitLosses | decimal | x |  | C |  |  |  |  | DBvalue/ calculation to be defined |  |  | Short-circuit losses
| NoLoadLosses | decimal | x |  | C |  |  |  |  | DBvalue/ calculation to be defined |  |  | No-load losses
ResultParameter | [12 empty] | Result parameter
| R1maxTrafo | decimal | x | [6 empty] | 09-01 |  |  | R1max [mΩ]
| X1maxTrafo | decimal | x | [6 empty] | 09-02 |  |  | X1max [mΩ]
| R0maxTrafo | decimal | x | [6 empty] | 09-03 |  |  | R0max [mΩ]
| X0maxTrafo | decimal | x | [6 empty] | 09-04 |  |  | X0max [mΩ]
| absVoltageDropTrafo | decimal | x | [6 empty] | 09-05 |  |  | ΔU tr [V]

## ClassStaticLoad
Class name | StaticLoad | [11 empty] | Localization
Group name | Characteristic | Type | Input Mandatory | enumerable | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
RequirementParameter | [12 empty] | Requirement parameter
| NumberPoles | choice | x | x | [8 empty] | Number of poles
[6 empty] | 1PLUSN | [6 empty] | 1+N
[6 empty] | 3 | [6 empty] | 3
[5 empty] | x | 3PLUSN | [6 empty] | 3+N
| Phases | choice | x | x | [8 empty] | Phases
[5 empty] | x | L1_L2_L3_N | [6 empty] | L1-L2-L3-N
[6 empty] | L1_L2_L3 | [6 empty] | L1-L2-L3
[6 empty] | L2_N | [6 empty] | L2-N
[6 empty] | L3_N | [6 empty] | L3-N
[6 empty] | L1_N | [6 empty] | L1-N
| LoadType | choice | x | x | [8 empty] | Type of load, ind/cap.
[5 empty] | x | inductive |  |  |  |  | -1 |  | inductive
[6 empty] | capacitive |  |  |  |  | 1 |  | capacitive
NetworkParameter | [12 empty] | Network parameter
| NominalVoltageLoad | decimal | x |  | C |  | C | C |  | to be defined |  |  | Nominal voltage Load [V]
RequirementAndResultParameter | [12 empty] | Requirement and Result parameter
| InStaticLoad | decimal | x |  |  |  | C | C |  | 10-01 |  |  | Nominal current Load [A]
[5 empty] | x | 200
| ActivePower | decimal | x |  | C |  | 0.055 | 2000 |  | 10-02 |  |  | Pn
| Quantity | decimal | x | [6 empty] | 0024 |  |  | Quantity

## types (hidden)
data types
char
boolean
numeric

## ERP Org (hidden)
Sales Org |  |  | Distribution Channel |  |  |  | Plant
0001 | SL Wetzlar | 0001 SL Wetzlar | 01 | Wz:BO Maschinen | Wz:Opht.Opt.Machines | 01 Wz:Opht.Opt.Machines | 0001 | Satisloh GmbH Brillenoptik | 0001 Satisloh GmbH Brillenoptik
0002 | LOH Oensingen | 0002 LOH Oensingen | 02 | Wz:Consumables | Wz:Consumables | 02 Wz:Consumables | 0002 | Satisloh Oensingen AG-obsolet | 0002 Satisloh Oensingen AG-obsolet
0003 | SL Baar | 0003 SL Baar | 03 | Wz:BO Dienstleistung | Wz:Opht.Opt.Services | 03 Wz:Opht.Opt.Services | 0003 | Satisloh AG | 0003 Satisloh AG
0004 | SL France | 0004 SL France | 04 | LOH Oensingen | LOH Oensingen | 04 LOH Oensingen | 0004 | Satisloh France S.A.S. | 0004 Satisloh France S.A.S.
0005 | SL USA | 0005 SL USA | 11 | Wz:FO Dienstleistung | Wz:Prec.Opt.Services | 11 Wz:Prec.Opt.Services | 0005 | Satisloh North America Inc. | 0005 Satisloh North America Inc.
0006 | SL Hongkong | 0006 SL Hongkong | 12 | Wz:FO Maschinen | Wz:Prec.Opt.Machines | 12 Wz:Prec.Opt.Machines | 0006 | Satisloh Asia Ltd. | 0006 Satisloh Asia Ltd.
0007 | SL Zhongshan | 0007 SL Zhongshan | 18 | SL Danyang | SL Danyang | 18 SL Danyang | 0007 | Satisloh Zhongshan | 0007 Satisloh Zhongshan
0008 | SL Settimo | 0008 SL Settimo | 30 | SL Baar | SL Baar | 30 SL Baar | 0008 | Satisloh Italy S.r.l. | 0008 Satisloh Italy S.r.l.
0009 | SL Horgen | 0009 SL Horgen | 40 | SL France | SL France | 40 SL France | 0009 | Satisloh Photonics AG | 0009 Satisloh Photonics AG
0018 | SL Danyang | 0018 SL Danyang | 50 | SL USA | SL USA | 50 SL USA | 0011 | Satisloh GmbH Feinoptik | 0011 Satisloh GmbH Feinoptik
|  |  | 60 | SL Hongkong | SL Hongkong | 60 SL Hongkong | 0018 | Satisloh Danyang | 0018 Satisloh Danyang
|  |  | 70 | SL Zhongshan | SL Zhongshan | 70 SL Zhongshan | 001S | SL GmbH Spain | 001S SL GmbH Spain
|  |  | 80 | SL Settimo | SL Settimo | 80 SL Settimo | 005C | Satisloh Warehouse Canada | 005C Satisloh Warehouse Canada
|  |  | 90 | SL Horgen | SL Horgen | 90 SL Horgen