## Sheet1
Short-Circuit Summary Report
3-Phase, LG, LL, LLG Fault Currents (all fault values in kA)
| Bus |  | 3-Phase |  | Line-to-Ground |  | Line-to-Line
| ID | kV | IpK | Ik3max | Ib | Ik1max | Ib | Ikmax2
| *L1* | 0.4 | 128.816 | 56.142 | 57.099 | 57.099 | 52.689 | 110.255
| *L2* | 0.4 | 96.576 | 46.555 | 43.543 | 43.543 | 42.692 | 82.81
| *L3* | 0.4 | 68.079 | 35.633 | 30.798 | 30.798 | 32.18 | 58.503
| *L4* | 0.4 | 71.362 | 40.679 | 37.007 | 37.007 | 36.821 | 61.231
| *L5* | 0.4 | 58.733 | 35.173 | 31.025 | 31.025 | 31.573 | 50.456
| PRI TR | 13.8 | 31.874 | 20.918 | 15.882 | 15.882 | 15.695 | 23.761
| SEC TR | 0.4 | 143.236 | 61.544 | 65.113 | 65.113 | 57.262 | 122.491
| SWB | 0.4 | 137.45 | 59.098 | 61.373 | 61.373 | 55.215 | 117.593
Sequence Impedance Summary Report
Bus |  | Positive Seq. Imp. (ohm) |  |  | Negative Seq. Imp. (ohm) |  |  | Zero Seq. Imp. (ohm)
ID | kV | R1 | X1 | Z1 | R2 | X2 | Z2 | R0 | X0 | Z0
*L1* | 0.4 | 0.00103 | 0.004 | 0.00413 | 0.00103 | 0.004 | 0.00413 | 0.001 | 0.0047 | 0.00481
*L2* | 0.4 | 0.00167 | 0.00482 | 0.0051 | 0.00167 | 0.00482 | 0.0051 | 0.002 | 0.00671 | 0.007
*L3* | 0.4 | 0.00273 | 0.00621 | 0.00678 | 0.00273 | 0.00621 | 0.00678 | 0.00368 | 0.01024 | 0.01088
*L4* | 0.4 | 0.00311 | 0.00503 | 0.00592 | 0.00311 | 0.00503 | 0.00592 | 0.0043 | 0.00725 | 0.00843
*L5* | 0.4 | 0.00409 | 0.00557 | 0.00691 | 0.00409 | 0.00557 | 0.00691 | 0.00585 | 0.00861 | 0.01041
PRI TR | 13.8 | 0.29353 | 0.29516 | 0.41627 | 0.29353 | 0.29516 | 0.41627 | 0.29626 | 0.29626 | 0.41897
SEC TR | 0.4 | 0.00086 | 0.00369 | 0.00379 | 0.00086 | 0.00369 | 0.00379 | 0.00063 | 0.00378 | 0.00384
SWB | 0.4 | 0.00091 | 0.00383 | 0.00394 | 0.00091 | 0.00383 | 0.00394 | 0.00079 | 0.00419 | 0.00426

## Sheet1 (2)
| Project: | Red Sea Mall |  |  |  | Page: | 1
| Location: | Riyadh,KSA |  |  |  | Date: | 13.06.2016
| Contract: | Red Sea market company |  |  |  | SN: | AL-FANAR02
| Engineer: | Omar Al-Khalifaa |  |  |  | Revision: | Base
${AnalyticData.label}
3-Phase, LG, LL, LLG Fault Currents (all fault values in kA)
| Bus |  | 3-Phase |  | Line to Ground |  | Line-to-Line
| ID | Un | Ik3max | Ipk | Ik1max ph(n) | Ik1max ph(pen) | Ik2min
<jx:forEach items="${AnalyticData.definesData}" var="data">
| ${data.breakerId} | ${data.kV} | ${data.Ik3max} | ${data.IpK} | ${data.Ik1max} | ${data.Ibltl} | ${data.Ik2min}
</jx:forEach>