## question
Any | Designation (ClassAny) an allen relevanten Unterstromkreisen pflegn? -- untersch Defaultwert
preferences | VoltageFactorCMax
VoltageFactorCMin und Max --> derzeit nur 1 Merkmale aber untersch. Default für LV und MV, moment nicht adäquat im Modell enthalten
Circuit | SystemConfiguration
derzeit nur 1 Merkmal aber untersch. Default für StLoad und circuit, moment nicht adäquat im Modell enthalten
ClassInfeed | NominalApparentPower
Defaultwert und Range sind erfunden--> Zulieferung durch Kunden nötig
ClassConsumer
cosPhi--> derzeit nur 1 Merkmal aber untersch. Quellen des aktuellen Wertes für StLoad (eingabe) und rest (Kalkulation)
Allgemein:
in aktueller Datei (und cistic Overview) Rules für alle kalkulierten Werte hinterlegen
Dokumentation der Quelle des aktuellen Wertes in Overview Cistic überabeiten, --> kann unter Rule hinterlegt sein (entweder Fornel oder Dbvalue)

## Revision
Date | Description | Version | Author | Status Implementation | Status Product Knowledge | Change Valid From in ERP | Knowledge Base Version CRM
2016-04-15 | Document created | 0.1 | K.Heylen | not implemented
2016-04-22 | Formula "links" added | 0.6 | M.Berbig | not implemented

## Taxonomy
Class | SuperClass | Label |  | Comment
|  | EN | DE | EN | DE
General | KnowledgeBase | General |  | Comment_General
ElectricalDesignDocument | General | ElectricalDesignDocument |  | Comment_ElectricalDesignDocument
Impedance | General | Impedance |  | Comment_Impedance
Circuit | General | Circuit |  | Comment_Circuit
DataPoint | General | DataPoint |  | Comment_DataPoint
MVInfeed | General | MVInfeed |  | Comment_MVInfeed
Infeed | Impedance | Infeed |  | Comment_Infeed
Connection | General | Connection |  | Comment_Connection
Consumer | Impedance | Consumer |  | Comment_Consumer
Metering | DataPoint | Metering |  | Comment_Metering
Switch | General | Switch |  | Comment_Switch
Transformer | Infeed | Transformer |  | Comment_Transformer
CableLV | Connection, Impedance | CableLV |  | Comment_CableLV
CableMV | Connection | CableMV |  | Comment_CableMV
GeneralLoad | Consumer | General Load |  | Comment_StaticLoad
Motor | Consumer | Motor |  | Comment_Motor
BreakerLV | Switch, DataPoint | BreakerLV |  | Comment_BreakerLV
BreakerMV | General | BreakerMV |  | Comment_BreakerMV
MCB | BreakerLV | MCB |  | Comment_MCB

## KBInstances
ObjectName | Class | Type | Parts | Label |  | Comment
|  |  |  | EN | DE | EN | DE
Transformer | Transformer | DesignStencil |  | Transformer |  | Comment_Transformer
MSnet | Infeed | DesignStencil |  | MSnet |  | Comment_MSnet
Generator | Infeed | DesignStencil |  | Generator |  | Comment_Generator
CableLV | CableLV | DesignStencil |  | CableLV |  | Comment_CableLV
CableMV | CableMV | DesignStencil |  | CableMV |  | Comment_CableMV
Busway | DataPoint | DesignStencil |  | Busway |  | Comment_Busway
GeneralLoad | GeneralLoad | DesignStencil |  | General Load |  | Comment_GeneralLoad
Motor | Motor | DesignStencil |  | Motor |  | Comment_Motor
Fuse | BreakerLV | DesignStencil |  | BreakerLV |  | Comment_Fuse
BreakerMV | BreakerMV | DesignStencil |  | BreakerMV |  | Comment_BreakerMV
MCB | BreakerLV | DesignStencil |  | BreakerLV |  | Comment_MCB
RCD | Switch | DesignStencil |  | RCD |  | Comment_RCD
MVInfeed | MVInfeed | DesignStencil |  | MVInfeed
ElectricalDesignDocument | ElectricalDesignDocument | DesignDocumentType |  | Electrical Design Document |  | Comment_ElectricalDesignDocument
TransformerCircuitLV | Circuit | DesignCompound | Transformer, CableLV, Fuse | Transformer Circuit |  | Comment_TransformerCircuitLV
BuswayCircuit | Circuit | DesignCompound | Busway | Busbar |  | Comment_BuswayCircuit
ConsumerCircuitLV | Circuit | DesignCompound | MCB, CableLV, GeneralLoad | General Load Circuit |  | Comment_ConsumerCircuitLV
SubDistributionCircuit | Circuit | DesignCompound | MCB, CableLV, Fuse | Sub Distribution |  | Comment_SubDistributionCircuit
MotorCircuitLV | Circuit | DesignCompound | MCB, CableLV, Motor | Motor Circuit |  | Comment_ConsumerCircuitLV
MVInfeedCircuit | General | DesignCompound | MVInfeed, BreakerMV, CableMV | MVInfeed Circuit |  | Comment_MVInfeedCircuit

## ClassGeneral
Class name | General | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| Designation | char | 1 | x | [9 empty] | Designation
[6 empty] | x | name | [6 empty] | Name

## ClassMVInfeed
Class name | MVInfeed | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| AmbientTemperature | decimal | 1 | x | [6 empty] | Copy From Design Document |  |  | Ambient temperature [°C]
| VoltageFactorCMax | decimal | 2 | x | [6 empty] | Copy From Design Document |  |  | Voltage factor c max
| VoltageFactorCMinMV | decimal | 3 | x | [6 empty] | Copy From Design Document |  |  | Voltage factor c minMV
| VoltageFactorCMinLV | decimal | 4 | x | [6 empty] | Copy From Design Document |  |  | Voltage factor c minLV
| RelationR1_X1min | decimal | 5 | x | [6 empty] | Copy From Design Document |  |  | Relation R1/X1 min
| RelationZ0_Z1min | decimal | 6 | x | [6 empty] | Copy From Design Document |  |  | Relation Z0/Z1 min
| RelationR0_X0min | decimal | 7 | x | [6 empty] | Copy From Design Document |  |  | Relation R0/X0 min
| NominalVoltageMV | decimal | 8 | x | [6 empty] | Copy From Design Document |  |  | Nominal voltage medium voltage [V]
| NominalVoltageLV | decimal | 9 | x | [6 empty] | Copy From Design Document |  |  | Nominal voltage low voltage [V]
| MaxShortCircuitPower | decimal | 10 | x | [6 empty] | Copy From Design Document |  |  | Max. short-circuit power [MVA]
| MinShortCircuitPower | decimal | 11 | x | [6 empty] | Copy From Design Document |  |  | Min. short-circuit power [MVA]
| RefPtVoltDropCalculation | char | 12 | x | [6 empty] | Copy From Design Document |  |  | Reference point of voltage drop calculation
Transformer-primary terminals
Transformer-secondary terminals
| CondTempLVCable | decimal | 1 | x | [6 empty] | Copy From Design Document |  |  | θΔu [°C]
| CondTempLVCableBeginShortCircuit | decimal | 2 | x | [6 empty] | Copy From Design Document |  |  | θIkmax [°C]
| CondTempLVCableDiscon | decimal | 3 | x | [6 empty] | Copy From Design Document |  |  | θIkmin [°C]
InterimResults | [13 empty] | Interim Results
| R1maxMV | decimal | 1 | x | [6 empty] | Copy From Design Document |  |  | R1max [mΩ]
| X1maxMV | decimal | 2 | x | [6 empty] | Copy From Design Document |  |  | X1max [mΩ]
| Z1maxMV | decimal | 3 | x | [6 empty] | Copy From Design Document |  |  | Z1max [mΩ]
| R1minMV | decimal | 4 | x | [6 empty] | Copy From Design Document |  |  | R1min [mΩ]
| X1minMV | decimal | 5 | x | [6 empty] | Copy From Design Document |  |  | X1min [mΩ]
| Z1minMV | decimal | 6 | x | [6 empty] | Copy From Design Document |  |  | Z1min [mΩ]
| R0maxMV | decimal | 7 | x | [6 empty] | Copy From Design Document |  |  | R0max [mΩ]
| X0maxMV | decimal | 8 | x | [6 empty] | Copy From Design Document |  |  | X0max [mΩ]
| Z0maxMV | decimal | 9 | x | [6 empty] | Copy From Design Document |  |  | Z0max [mΩ]
| R0minMV | decimal | 10 | x | [6 empty] | Copy From Design Document |  |  | R0min [mΩ]
| X0minMV | decimal | 11 | x | [6 empty] | Copy From Design Document |  |  | X0min [mΩ]
| Z0minMV | decimal | 12 | x | [6 empty] | Copy From Design Document |  |  | Z0min [mΩ]

## ClassElectricalDesignDocument
Class name | ElectricalDesignDocument | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| AmbientTemperature | decimal | 1 | x |  |  |  | 30 | 60 |  |  |  |  | Ambient temperature [°C]
[6 empty] | x | 40
| VoltageFactorCMax | decimal | 2 | x |  |  |  | 1.1 | 1.1 |  |  |  |  | Voltage factor c max
[6 empty] | x | 1.1
| VoltageFactorCMinMV | decimal | 3 | x |  |  |  | 1 | 1 |  |  |  |  | Voltage factor c minMV
[6 empty] | x | 1
| VoltageFactorCMinLV | decimal | 4 | x |  |  |  | 0.95 | 0.95 |  |  |  |  | Voltage factor c minLV
[6 empty] | x | 0.95
| RelationR1_X1min | decimal | 5 | x |  |  |  | 0.2 | 0.2 |  |  |  |  | Relation R1/X1 min
[6 empty] | x | 0.2
| RelationZ0_Z1min | decimal | 6 | x |  |  |  | 1 | 1 |  |  |  |  | Relation Z0/Z1 min
[6 empty] | x | 1
| RelationR0_X0min | decimal | 7 | x |  |  |  | 1 | 1 |  |  |  |  | Relation R0/X0 min
[6 empty] | x | 1
| NominalVoltageMV | decimal | 8 | x |  |  |  | 5000 | 40000 |  |  |  |  | Nominal voltage medium voltage [V]
[6 empty] | x | 20000
| NominalVoltageLV | decimal | 9 | x |  |  |  | 200 | 1000 |  |  |  |  | Nominal voltage low voltage [V]
[6 empty] | x | 400
| MaxShortCircuitPower | decimal | 10 | x |  |  |  | 10 | 1000 |  |  |  |  | Max. short-circuit power [MVA]
[6 empty] | x | 250
| MinShortCircuitPower | decimal | 11 | x |  |  |  | 10 | 0,9*MaxShortCircuitPower |  |  |  |  | Min. short-circuit power [MVA]
[6 empty] | x | 100
| RefPtVoltDropCalculation | choice | 12 | x | [9 empty] | Reference point of voltage drop calculation
[6 empty] | x | TransformerPrimTerminals | [6 empty] | Transformer-primary terminals
[7 empty] | TransformerSecTerminals | [6 empty] | Transformer-secondary terminals
| CondTempLVCable | decimal | 1 | x |  |  |  | 0 | 100 |  |  |  |  | θΔu [°C]
[6 empty] | x | 50
| CondTempLVCableBeginShortCircuit | decimal | 2 | x |  |  |  | 20 | 20 |  |  |  |  | θIkmax [°C]
[6 empty] | x | 20
| CondTempLVCableDiscon | decimal | 3 | x |  |  |  | 0 | 250 |  |  |  |  | θIkmin [°C]
[6 empty] | x | 70
InterimResults | [13 empty] | Interim Results
| R1maxMV | decimal | 1 | x | x | [5 empty] | 00-01 |  |  | R1max [mΩ]
| X1maxMV | decimal | 2 | x | x | [5 empty] | 00-02 |  |  | X1max [mΩ]
| Z1maxMV | decimal | 3 | x | x | [5 empty] | 00-03 |  |  | Z1max [mΩ]
| R1minMV | decimal | 4 | x | x | [5 empty] | 00-04 |  |  | R1min [mΩ]
| X1minMV | decimal | 5 | x | x | [5 empty] | 00-05 |  |  | X1min [mΩ]
| Z1minMV | decimal | 6 | x | x | [5 empty] | 00-06 |  |  | Z1min [mΩ]
| R0maxMV | decimal | 7 | x | x | [5 empty] | 00-07 |  |  | R0max [mΩ]
| X0maxMV | decimal | 8 | x | x | [5 empty] | 00-08 |  |  | X0max [mΩ]
| Z0maxMV | decimal | 9 | x | x | [5 empty] | 00-09 |  |  | Z0max [mΩ]
| R0minMV | decimal | 10 | x | x | [5 empty] | 00-10 |  |  | R0min [mΩ]
| X0minMV | decimal | 11 | x | x | [5 empty] | 00-11 |  |  | X0min [mΩ]
| Z0minMV | decimal | 12 | x | x | [5 empty] | 00-12 |  |  | Z0min [mΩ]

## ClassImpedance
Class name | Impedance | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| operatingCurrent | decimal | 4 | x |  | C |  | C | C |  | 01-01 |  |  | Operating current [A]
| loadCurrent | decimal | 5 | x |  | C |  | C | C |  | 01-02 |  |  | Load current [A]
| RatedEffectivePower | decimal | 13 | x | [6 empty] | 01-18 |  |  | P [kW]
| ReactivePower | decimal | 14 | x | [6 empty] | 01-19 |  |  | Q [kvar]
| RatedPower | decimal | 15 | x | [6 empty] | 01-20 |  |  | S [kVA]

## ClassCircuit
Class name | Circuit | [13 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment |  | EN | DE
Parameter | [14 empty] | Parameter
| SystemConfiguration | choice | 13 | x | [10 empty] | Earthing System
[7 empty] | TN_S | [7 empty] | TN-S
[6 empty] | x | TN_C | [7 empty] | TN-C
[7 empty] | IT | [7 empty] | IT
[7 empty] | TT | [7 empty] | TT
| Quantity | int | 14 | x | x | [9 empty] | Quantity
[6 empty] | x | 1
| SimultaneityFactor | decimal | 6 | x |  |  |  | 0 | 1 | [5 empty] | Simultaneity factor
[6 empty] | x | 1
| LoadTypeFactor | decimal | 12 | x | x | [5 empty] | 12-01 |  |  | Type of load, ind/cap. | Load Type Factor
| cosPhi | decimal | 13 | x |  |  |  | 0.1 | 1 |  | 12-02 |  |  | cos φ | cos φ
| RelativeVoltageDrop | decimal | 14 | x |  | C |  | 0 | 100 |  | 01-03 |  |  |  | Δu [%]
| RelativeCumVoltageDrop | decimal | 15 | x |  | C |  | 0 | 100 |  | 01-04 |  |  |  | ∑Δu [%]
| absVoltageDrop | decimal | 32 | x | [6 empty] | Sum of all Children |  |  | ΔU [V] | ΔU [V]
| sumAbsVoltageDrop | decimal | 33 | x | [6 empty] | 01-17 |  |  |  | ΣΔU [V]
InterimResults | [14 empty] | Interim Results
| totalActiveCurrent | decimal | 7 | x | [6 empty] | 02-26 |  |  | Igw [A] | Igw [A]
| totalReactiveCurrent | decimal | 8 | x | [6 empty] | 02-27 |  |  | Igb [A] | Igb [A]
| totalApparantCurrent | decimal | 9 | x | [6 empty] | 02-28 |  |  | Igs [A] | Igs [A]
| activeLoadCurrent | decimal | 10 | x | [6 empty] | 02-29 |  |  | Ibw [A] | Ibw [A]
| reactiveLoadCurrent | decimal | 11 | x | [6 empty] | 02-30 |  |  | Ibb [A] | Ibb [A]
| R1max | decimal | 16 | x | [6 empty] | 01-05 |  |  |  | R1max [mΩ]
| X1max | decimal | 17 | x | [6 empty] | 01-06 |  |  |  | X1max [mΩ]
| Z1max | decimal | 18 | x | [6 empty] | 01-07 |  |  |  | Z1max [mΩ]
| R0ph_n_max | decimal | 19 | x | [6 empty] | 01-08 |  |  |  | R0maxph-n [mΩ]
| R0ph_pen_max | decimal | 20 | x | [6 empty] | 01-09 |  |  |  | R0maxph-pe(n) [mΩ]
| Z0max | decimal | 21 | x | [6 empty] | 01-10 |  |  |  | Z0max [mΩ]
| R1min | decimal | 22 | x | [6 empty] | 01-11 |  |  |  | R1min [mΩ]
| X1min | decimal | 23 | x | [6 empty] | 01-12 |  |  |  | X1min [mΩ]
| Z1min | decimal | 24 | x | [6 empty] | 01-13 |  |  |  | Z1min [mΩ]
| R0ph_n_min | decimal | 25 | x | [6 empty] | 01-14 |  |  |  | R0minph-n [mΩ]
| R0ph_pen_min | decimal | 26 | x | [6 empty] | 01-15 |  |  |  | R0minph-pe(n) [mΩ]
| Z0min | decimal | 27 | x | [6 empty] | 01-16 |  |  |  | Z0min [mΩ]
| X0ph_n_max | decimal | 28 | x | [6 empty] | 01-21 |  |  |  | X0maxph-n [mΩ]
| X0ph_pen_max | decimal | 29 | x | [6 empty] | 01-22 |  |  |  | X0maxph-pe(n) [mΩ]
| X0ph_n_min | decimal | 30 | x | [6 empty] | 01-23 |  |  |  | X0minph-n [mΩ]
| X0ph_pen_min | decimal | 31 | x | [6 empty] | 01-24 |  |  |  | X0minph-pe(n) [mΩ]

## ClassDataPoint
Class name | DataPoint | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| Ik3max | decimal | 34 | x | [6 empty] | 02-01 |  |  | Ik3max [kA]
| Ik1maxph_n | decimal | 35 | x | [6 empty] | 02-02 |  |  | Ik1maxph_n [kA]
| Ik1maxph_pe | decimal | 36 | x | [6 empty] | 02-03 |  |  | Ik1maxph_pe [kA]
| maxAsymShortCircuitCurrent | decimal | 37 | x | [6 empty] | 02-04 |  |  | Ipk [kA]
| Ik3min | decimal | 38 | x | [6 empty] | 02-05 |  |  | Ik3min [kA]
| Ik2min | decimal | 39 | x | [6 empty] | 02-06 |  |  | Ik2min [kA]
| Ik1minph_n | decimal | 40 | x | [6 empty] | 02-07 |  |  | Ik1minph_n [kA]
| Ik1minph_pe | decimal | 41 | x | [6 empty] | 02-08 |  |  | Ik1minph_pe [kA]
| phaseAngleIk3max | decimal | 42 | x | [6 empty] | 02-09 |  |  | φ3_max [°]
| phaseAngleIk1maxph_n | decimal | 43 | x | [6 empty] | 02-10 |  |  | φ1ph_n_max [°]
| phaseAngleIk1maxph_pe | decimal | 44 | x | [6 empty] | 02-11 |  |  | φ1ph_pe_max [°]
| phaseAngleIk3min | decimal | 45 | x | [6 empty] | 02-12 |  |  | φ3_min [°]
| phaseAngleIk2min | decimal | 46 | x | [6 empty] | 02-13 |  |  | φ2_min [°]
| phaseAngleIk1minph_n | decimal | 47 | x | [6 empty] | 02-14 |  |  | φ1ph_n_min [°]
| phaseAngleIk1minph_pe | decimal | 48 | x | [6 empty] | 02-15 |  |  | φ1ph_pe_min [°]
| Ikmin | decimal | 49 | x | [6 empty] | 02-24 |  |  | Ikmin [kA]
| Ikmax | decimal | 50 | x | [6 empty] | 02-25 |  |  | Ikmax [kA]
InterimResults | [15 empty] | Interim Results
| R1max | decimal | 1 | x | [6 empty] | Circuit value without children values |  |  | R1max [mΩ] |  | R1max [mΩ]
| X1max | decimal | 2 | x | [6 empty] | Circuit value without children values |  |  | X1max [mΩ] |  | X1max [mΩ]
| R0ph_n_max | decimal | 3 | x | [6 empty] | Circuit value without children values |  |  | R0maxph-n [mΩ] |  | R0maxph-n [mΩ]
| R0ph_pen_max | decimal | 4 | x | [6 empty] | Circuit value without children values |  |  | R0maxph-pe(n) [mΩ] |  | R0maxph-pe(n) [mΩ]
| R1min | decimal | 5 | x | [6 empty] | Circuit value without children values |  |  | R1min [mΩ] |  | R1min [mΩ]
| X1min | decimal | 6 | x | [6 empty] | Circuit value without children values |  |  | X1min [mΩ] |  | X1min [mΩ]
| R0ph_n_min | decimal | 7 | x | [6 empty] | Circuit value without children values |  |  | R0minph-n [mΩ] |  | R0minph-n [mΩ]
| R0ph_pen_min | decimal | 8 | x | [6 empty] | Circuit value without children values |  |  | R0minph-pe(n) [mΩ] |  | R0minph-pe(n) [mΩ]
| X0ph_n_max | decimal | 9 | x | [6 empty] | Circuit value without children values |  |  | X0maxph-n [mΩ] |  | X0maxph-n [mΩ]
| X0ph_pen_max | decimal | 10 | x | [6 empty] | Circuit value without children values |  |  | X0maxph-pe(n) [mΩ] |  | X0maxph-pe(n) [mΩ]
| X0ph_n_min | decimal | 11 | x | [6 empty] | Circuit value without children values |  |  | X0minph-n [mΩ] |  | X0minph-n [mΩ]
| X0ph_pen_min | decimal | 12 | x | [6 empty] | Circuit value without children values |  |  | X0minph-pe(n) [mΩ] |  | X0minph-pe(n) [mΩ]

## ClassInfeed
Class name | Infeed | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| NominalApparentPower | decimal | 16 | x | x |  |  | 50 | 8000 |  | Modelled |  |  | Nominal (apparent) power [kVA]
InterimResults | [13 empty] | Interim Results
| Ibem | decimal | 51 | x | [6 empty] | 03-01 |  |  | Ibem [A]

## ClassConnection
Class name | Connection | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| Material | choice | 18 | x | x | [8 empty] | Material
[6 empty] | x | Copper |  |  |  |  | 0.00393 |  | Cu
[7 empty] | Aluminum |  |  |  |  | 0.00403 |  | Al
| Length | decimal | 19 | x |  |  |  | 0.1 | 10000 |  |  |  |  | Length [m]
| CrossSectionPhaseConductor | decimal | 20 | x | [6 empty] | Modelled |  |  | Cross section of phase conductor [mm2]
[6 empty] | x | [7 empty] | Basic data
| ftot | decimal | 21 | x |  |  |  | 0 | 2 |  |  |  |  | Correction Factor
[6 empty] | x | 1
| currentCarryingCapacity | decimal | 3 | x |  | C |  |  |  |  | 13-01 |  |  | Iz [A]
InterimResults | [13 empty] | Interim Results
| conResPhaseCondPerUnitLength20Degr | decimal | 1 | x |  | C |  |  |  |  | Modelled |  |  | r1 [mΩ/m]
| conReactPhaseCondPerUnitLength | decimal | 2 | x |  | C |  |  |  |  | Modelled |  |  | x1 [mΩ/m]

## ClassCableMV
Class name | CableMV | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| NumberRuns | decimal | 22 | x |  |  |  | 1 | 20 |  |  |  |  | Number of runs
[6 empty] | x | 1
| Ik2min_F2 | decimal | 60 | x | [6 empty] | 02-18 |  |  | Ik2min(F2) [kA]
| AllowedLoadCapacity | choice | 17 | x | [9 empty] | Allowed load capacity
[7 empty] | 151 |  |  |  |  | 151 |  | 151 A
[7 empty] | 178 |  |  |  |  | 178 |  | 178 A
[7 empty] | 217 |  |  |  |  | 217 |  | 217 A
[7 empty] | 258 |  |  |  |  | 258 |  | 258 A
[7 empty] | 291 |  |  |  |  | 291 |  | 291 A
[7 empty] | 326 |  |  |  |  | 326 |  | 326 A
[7 empty] | 366 |  |  |  |  | 366 |  | 366 A
[7 empty] | 421 |  |  |  |  | 421 |  | 421 A
[7 empty] | 473 |  |  |  |  | 473 |  | 473 A
[7 empty] | 530 |  |  |  |  | 530 |  | 530 A
[7 empty] | 592 |  |  |  |  | 592 |  | 592 A
InterimResults | [13 empty] | Interim Results
| r0 | decimal | 4 | x | [6 empty] | Modelled |  |  | r0 [mΩ/m]
| x0 | decimal | 5 | x | [6 empty] | Modelled |  |  | x0 [mΩ/m]
| R1max | decimal | 52 | x | [6 empty] | 04-01 |  |  | R1max [mΩ]
| X1max | decimal | 53 | x | [6 empty] | 04-02 |  |  | X1max [mΩ]
| R0max | decimal | 54 | x | [6 empty] | 04-03 |  |  | R0max [mΩ]
| X0max | decimal | 55 | x | [6 empty] | 04-04 |  |  | X0max [mΩ]
| R1min | decimal | 56 | x | [6 empty] | 04-05 |  |  | R1min [mΩ]
| X1min | decimal | 57 | x | [6 empty] | 04-06 |  |  | X1min [mΩ]
| R0min | decimal | 58 | x | [6 empty] | 04-07 |  |  | R0min [mΩ]
| X0min | decimal | 59 | x | [6 empty] | 04-08 |  |  | X0min [mΩ]

## ClassCableLV
Class name | CableLV | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| InstallationType | choice | 23 | x | [9 empty] | Installation type
[7 empty] | A2 | [6 empty] | A2
[7 empty] | B1 | [6 empty] | B1
[7 empty] | B2 | [6 empty] | B2
[6 empty] | x | C | [6 empty] | C
[7 empty] | D1 | [6 empty] | D1
[7 empty] | D2 | [6 empty] | D2
[7 empty] | E | [6 empty] | E
| PermisVoltageDropPerSection | decimal | 24 | x |  |  |  | 0 | 20 |  |  |  |  | Permissable voltage drop / section [%]
[6 empty] | x | 4
| NumberRuns | decimal | 25 | x |  |  |  | 1 | 20 |  |  |  |  | Number of runs
[6 empty] | x | 1
| CrossSectionNConductor | decimal | 26 | x |  | C |  | 1.5 | 630 |  | Modelled |  |  | Cross section of N conductor [mm2]
| CrossSectionPEConductor | decimal | 27 | x |  | C |  | 1.5 | 630 |  | Modelled |  |  | Cross section of PE conductor [mm2]
| absVoltageDrop | decimal | 77 | x | [6 empty] | 05-13 |  |  | ΔU [V]
| Ik2min_F4 | decimal | 80 | x | [6 empty] | 02-22 |  |  | Ik2min(F4) [kA]
| Ik1min_F4 | decimal | 81 | x | [6 empty] | 02-23 |  |  | Ik1min(F4) [kA]
| AllowedLoadCapacity | choice | 17 | x | [9 empty] | Allowed load capacity
[7 empty] | 17_5 |  |  |  |  | 17.5 |  | 17.5 A
[7 empty] | 24 |  |  |  |  | 24 |  | 24 A
[7 empty] | 32 |  |  |  |  | 32 |  | 32 A
[7 empty] | 41 |  |  |  |  | 41 |  | 41 A
[7 empty] | 57 |  |  |  |  | 57 |  | 57 A
[7 empty] | 76 |  |  |  |  | 76 |  | 76 A
[7 empty] | 96 |  |  |  |  | 96 |  | 96 A
[7 empty] | 119 |  |  |  |  | 119 |  | 119 A
[7 empty] | 144 |  |  |  |  | 144 |  | 144 A
[7 empty] | 184 |  |  |  |  | 184 |  | 184 A
[7 empty] | 223 |  |  |  |  | 223 |  | 223 A
[7 empty] | 259 |  |  |  |  | 259 |  | 259 A
[7 empty] | 299 |  |  |  |  | 299 |  | 299 A
[7 empty] | 341 |  |  |  |  | 341 |  | 341 A
[7 empty] | 403 |  |  |  |  | 403 |  | 403 A
[7 empty] | 464 |  |  |  |  | 464 |  | 464 A
InterimResults | [13 empty] | Interim Results
| R1DeltaU | decimal | 61 | x | [6 empty] | 05-14 |  |  | R1ΔU [mΩ]
| X1DeltaU | decimal | 62 | x | [6 empty] | 05-15 |  |  | X1ΔU [mΩ]
| R0ph_nDeltaU | decimal | 63 | x | [6 empty] | 05-16 |  |  | R0ph-nΔU [mΩ]
| X0ph_nDeltaU | decimal | 64 | x | [6 empty] | 05-17 |  |  | X0ph-nΔU [mΩ]
| R1max | decimal | 65 | x | [6 empty] | 05-01 |  |  | R1max [mΩ]
| X1max | decimal | 66 | x | [6 empty] | 05-02 |  |  | X1max [mΩ]
| R0ph_n_max | decimal | 67 | x | [6 empty] | 05-03 |  |  | R0ph-nmax [mΩ]
| R0ph_pe_n_max | decimal | 68 | x | [6 empty] | 05-04 |  |  | R0ph-pe(n)max [mΩ]
| R1min | decimal | 69 | x | [6 empty] | 05-05 |  |  | R1min [mΩ]
| X1min | decimal | 70 | x | [6 empty] | 05-06 |  |  | X1min [mΩ]
| R0ph_n_min | decimal | 71 | x | [6 empty] | 05-07 |  |  | R0ph-nmin [mΩ]
| R0ph_pe_n_min | decimal | 72 | x | [6 empty] | 05-08 |  |  | R0ph-pe(n)min [mΩ]
| X0ph_n_min | decimal | 73 | x | [6 empty] | 05-09 |  |  | X0ph-nmin [mΩ]
| X0ph_pe_n_min | decimal | 74 | x | [6 empty] | 05-10 |  |  | X0ph-pe(n)min [mΩ]
| IbemInfeed | decimal | 75 | x | [6 empty] | 05-11 |  |  | Ibem infeed cable [A]
| Ibem | decimal | 76 | x | [6 empty] | 05-12 |  |  | Ibem cable [A]
| X0ph_n_max | decimal | 78 | x | [6 empty] | 05-18 |  |  | X0ph-nmax [mΩ]
| X0ph_pe_n_max | decimal | 79 | x | [6 empty] | 05-19 |  |  | X0ph-pe(n)max [mΩ]
| r0ph_n | decimal | 6 | x |  | C |  |  |  |  | Modelled |  |  | r0ph-n [mΩ/m]
| r0ph_pe_n | decimal | 7 | x |  | C |  |  |  |  | Modelled |  |  | r0ph-pe(n) [mΩ/m]
| x0ph_n | decimal | 8 | x |  | C |  |  |  |  | Modelled |  |  | x0ph-n [mΩ/m]
| x0ph_pe_n | decimal | 9 | x |  | C |  |  |  |  | Modelled |  |  | x0ph-pe(n) [mΩ/m]

## ClassConsumer
Class name | Consumer | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| cosPhi | decimal | 28 | x |  |  |  | 0.1 | 1 |  |  |  |  | cos φ
[6 empty] | x | 0.8
| Capacity_LoadFactor | decimal | 29 | x |  |  |  | 0 | 1 |  |  |  |  | Capacity factor / load factor
[6 empty] | x | 1
| RatedEffectivePower | decimal | 88 | x | x | [5 empty] | 01-25 |  |  | P [kW]
| ReactivePower | decimal | 89 | x | x | [5 empty] | 01-26 |  |  | Q [kvar]
InterimResults | [13 empty] | Interim Results
| PhaseAngleIn | decimal | 82 | x | [6 empty] | 06-01 |  |  | phase angle In [°]
| totalActiveCurrent | decimal | 83 | x | [6 empty] | 02-31 |  |  | Igw [A]
| totalReactiveCurrent | decimal | 84 | x | [6 empty] | 02-32 |  |  | Igb [A]
| totalApparantCurrent | decimal | 85 | x | [6 empty] | 02-33 |  |  | Igs [A]
| activeLoadCurrent | decimal | 86 | x | [6 empty] | 02-34 |  |  | Ibw [A]
| reactiveLoadCurrent | decimal | 87 | x | [6 empty] | 02-35 |  |  | Ibb [A]

## ClassSwitch
Class name | Switch | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| Inswitch | decimal | 13 | x |  | C |  | 0.1 | 8000 |  | 07-06 |  |  | Nominal current In [A]
| Icu | decimal | 91 | x | [6 empty] | 07-02 |  |  | Icn/Icu [kA]
| Icm | decimal | 92 | x | [6 empty] | 07-03 |  |  | Icm [kA]
InterimResults | [13 empty] | Interim Results
| Ibem | decimal | 90 | x | [6 empty] | 07-01 |  |  | Ibem [A]

## ClassBreakerLV
Class name | BreakerLV | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| SwitchgearType | choice | 30 | x | [9 empty] | Type of switchgear low voltage
[7 empty] | none | [6 empty] | none
[6 empty] | x | Circuit-breaker | [6 empty] | Circuit-breaker
| I2 | decimal | 32 | x |  | C |  |  |  |  | 11-02 |  |  | I2 [A]
InterimResults | [13 empty] | Interim Results
| fcm | decimal | 31 | x | x | C |  |  |  |  | 11-01 |  |  | fcm

## ClassBreakerMV
Class name | BreakerMV | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| SwitchgearType | choice | 33 | x | [9 empty] | Type of switchgear medium voltage
[6 empty] | x | Circuit-breaker | [6 empty] | Circuit-breaker
| Ik1max_F1 | decimal | 93 | x | [6 empty] | 02-16 |  |  | Ik1max(F1) [kA]
| Ik3max_F1 | decimal | 94 | x | [6 empty] | 02-17 |  |  | Ik3max(F1) [kA]
| In | choice |  | x | [9 empty] | In
[7 empty] | 630 |  |  |  |  | 630 |  | 630 A
[7 empty] | 1250 |  |  |  |  | 1250 |  | 1250 A
[7 empty] | 2500 |  |  |  |  | 2500 |  | 2500 A
[7 empty] | 3150 |  |  |  |  | 3150 |  | 3150 A

## ClassMCB
Class name | MCB | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| Icn | decimal | 95 | x | [6 empty] | 08-01 |  |  | Icn/ Icu [kA]

## ClassTransformer
Class name | Transformer | [12 empty] | Localization
Group name | Characteristic | Type |  | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| RatedShortCircuitVoltage | decimal | 34 | x | [6 empty] | Modelled |  |  | Rated short-circuit voltage
| ShortCircuitLosses | decimal | 35 | x |  | C |  |  |  |  | Modelled |  |  | Short-circuit losses [kW]
| NoLoadLosses | decimal | 36 | x |  | C |  |  |  |  | Modelled |  |  | No-load losses [kW]
| absVoltageDrop | decimal | 100 | x | [6 empty] | 09-05 |  |  | ΔU tr [V]
| Ik3max_F3 | decimal | 101 | x | [6 empty] | 02-19 |  |  | Ik3max(F3) [kA]
| Ik2min_F3 | decimal | 102 | x | [6 empty] | 02-20 |  |  | Ik2min(F3) [kA]
| Ik1min_F3 | decimal | 103 | x | [6 empty] | 02-21 |  |  | Ik1min(F3) [kA]
| In | decimal | 14 |  |  | C |  | 0 | C |  | 01-27 |  |  | Nominal current [A]
| NominalApparentPower | choice | 16 | x | [9 empty] | Sn |  | Nominal (apparent) power [kVA]
[7 empty] | 100 |  |  |  |  | 100 |  | 100 kVA
[7 empty] | 200 |  |  |  |  | 200 |  | 200 kVA
[7 empty] | 300 |  |  |  |  | 300 |  | 300 kVA
[7 empty] | 500 |  |  |  |  | 500 |  | 500 kVA
[7 empty] | 1000 |  |  |  |  | 1000 |  | 1000 kVA
[7 empty] | 1500 |  |  |  |  | 1500 |  | 1500 kVA
[7 empty] | 2000 |  |  |  |  | 2000 |  | 2000 kVA
[7 empty] | 3150 |  |  |  |  | 3150 |  | 3150 kVA
InterimResults | [13 empty] | Interim Results
| R1max | decimal | 96 | x | [6 empty] | 09-01 |  |  | R1max [mΩ]
| X1max | decimal | 97 | x | [6 empty] | 09-02 |  |  | X1max [mΩ]
| R0max | decimal | 98 | x | [6 empty] | 09-03 |  |  | R0max [mΩ]
| X0max | decimal | 99 | x | [6 empty] | 09-04 |  |  | X0max [mΩ]

## ClassGeneralLoad
Class name | General Load | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| NumberPoles | choice | 37 | x | [9 empty] | Number of poles
[7 empty] | 1PLUSN |  |  |  |  | 1 |  | 1+N
[7 empty] | 3 |  |  |  |  | 1.7321 |  | 3
[6 empty] | x | 3PLUSN |  |  |  |  | 1.7321 |  | 3+N
| Phases | choice | 38 | x | [9 empty] | Phases
[6 empty] | x | L1_L2_L3_N | [6 empty] | L1-L2-L3-N
[7 empty] | L1_L2_L3 | [6 empty] | L1-L2-L3
[7 empty] | L2_N | [6 empty] | L2-N
[7 empty] | L3_N | [6 empty] | L3-N
[7 empty] | L1_N | [6 empty] | L1-N
| LoadType | choice | 39 | x | [9 empty] | Type of load, ind/cap.
[6 empty] | x | inductive |  |  |  |  | -1 |  | inductive
[7 empty] | capacitive |  |  |  |  | 1 |  | capacitive
| NominalVoltageLoad | decimal | 15 | x |  | C |  | C | C |  | 10-03 |  |  | Nominal voltage Load [V]
| InStaticLoad | decimal | 15 | x |  |  |  | C | C |  | 10-01 |  |  | Nominal current Load [A]
[6 empty] | x | 200
| ActivePower | decimal | 16 | x |  | C |  | 0.055 | 2000 |  | 10-02 |  |  | Pn [kW]

## types (hidden)
data types
char
boolean
numeric

## ERP Org (hidden)
Sales Org |  |  | Distribution Channel |  |  |  | Plant
0001 | SL Wetzlar | 0001 SL Wetzlar | 01 | Wz:BO Maschinen | Wz:Opht.Opt.Machines | 01 Wz:Opht.Opt.Machines | 0001 | Satisloh GmbH Brillenoptik | 0001 Satisloh GmbH Brillenoptik
0002 | LOH Oensingen | 0002 LOH Oensingen | 02 | Wz:Consumables | Wz:Consumables | 02 Wz:Consumables | 0002 | Satisloh Oensingen AG-obsolet | 0002 Satisloh Oensingen AG-obsolet
0003 | SL Baar | 0003 SL Baar | 03 | Wz:BO Dienstleistung | Wz:Opht.Opt.Services | 03 Wz:Opht.Opt.Services | 0003 | Satisloh AG | 0003 Satisloh AG
0004 | SL France | 0004 SL France | 04 | LOH Oensingen | LOH Oensingen | 04 LOH Oensingen | 0004 | Satisloh France S.A.S. | 0004 Satisloh France S.A.S.
0005 | SL USA | 0005 SL USA | 11 | Wz:FO Dienstleistung | Wz:Prec.Opt.Services | 11 Wz:Prec.Opt.Services | 0005 | Satisloh North America Inc. | 0005 Satisloh North America Inc.
0006 | SL Hongkong | 0006 SL Hongkong | 12 | Wz:FO Maschinen | Wz:Prec.Opt.Machines | 12 Wz:Prec.Opt.Machines | 0006 | Satisloh Asia Ltd. | 0006 Satisloh Asia Ltd.
0007 | SL Zhongshan | 0007 SL Zhongshan | 18 | SL Danyang | SL Danyang | 18 SL Danyang | 0007 | Satisloh Zhongshan | 0007 Satisloh Zhongshan
0008 | SL Settimo | 0008 SL Settimo | 30 | SL Baar | SL Baar | 30 SL Baar | 0008 | Satisloh Italy S.r.l. | 0008 Satisloh Italy S.r.l.
0009 | SL Horgen | 0009 SL Horgen | 40 | SL France | SL France | 40 SL France | 0009 | Satisloh Photonics AG | 0009 Satisloh Photonics AG
0018 | SL Danyang | 0018 SL Danyang | 50 | SL USA | SL USA | 50 SL USA | 0011 | Satisloh GmbH Feinoptik | 0011 Satisloh GmbH Feinoptik
|  |  | 60 | SL Hongkong | SL Hongkong | 60 SL Hongkong | 0018 | Satisloh Danyang | 0018 Satisloh Danyang
|  |  | 70 | SL Zhongshan | SL Zhongshan | 70 SL Zhongshan | 001S | SL GmbH Spain | 001S SL GmbH Spain
|  |  | 80 | SL Settimo | SL Settimo | 80 SL Settimo | 005C | Satisloh Warehouse Canada | 005C Satisloh Warehouse Canada
|  |  | 90 | SL Horgen | SL Horgen | 90 SL Horgen

## ClassMotor
Class name | Motor | [12 empty] | Localization
Group name | Characteristic | Type | sequenceID | Input Mandatory | Hidden | Default | Value | Value range min | Value range max | Component Selection | Rule | attributionFactor | Comment | EN | DE
Parameter | [13 empty] | Parameter
| MotorType | choice | 40 | x | [9 empty] | Type of motor
[7 empty] | MotorStarterCombination | [6 empty] | motor starter combination
[6 empty] | x | SimpleMotorProtection | [6 empty] | simple motor protection
| SwitchingDeviceType | choice | 41 | x | [6 empty] | Dbvalue |  |  | Type of switching device
[6 empty] | x | fuseless | [6 empty] | fuseless
[7 empty] | fused | [6 empty] | fused
| StartingMode | choice | 42 | x | [6 empty] | Dbvalue |  |  | StartingMode
[6 empty] | x | Direct | [6 empty] | Direct
[7 empty] | Reverse | [6 empty] | Reverse
[7 empty] | StarDelta | [6 empty] | Star Delta
[7 empty] | Soft | [6 empty] | Soft
| Co_ordinationType | choice | 43 | x | [6 empty] | Dbvalue |  |  | Co-ordinationType
[6 empty] | x | Type1 | [6 empty] | Type 1
[7 empty] | Type2 | [6 empty] | Type 2
| RelayType | choice | 44 | x | [6 empty] | Dbvalue |  |  | Type of Relay
[6 empty] | x | without | [6 empty] | without
[7 empty] | thermal | [6 empty] | thermal
[7 empty] | electronic | [6 empty] | electronic
| efficiency | decimal | 46 | x |  | x |  | 0.1 | 1 |  | DBvalue |  |  | η
| StartingCurrentRatio | decimal | 48 | x |  | x |  | 1 | 10 |  | Dbvalue |  |  | Ia/In
| R/X_ratio | decimal | 49 | x |  |  |  | 0.1 | 1 |  | Dbvalue |  |  | R/X-ratio
[6 empty] | x | 0.42
| Ik1 | decimal | 19 | x | [6 empty] | 15-03 |  |  | Ik1motor [kA]
| In | decimal | 20 | x |  | C |  | C | C |  | 15-04 |  |  | In_motor [A]
| Pmech | decimal | 21 | x |  |  |  | 0.1 | 1000 |  |  |  | In erster Instanz wird Pmech aus der Motor-DB gezogen | Pmech [kW]
[6 empty] | x | 15
| absVoltageDrop | decimal | 22 | x | [6 empty] | 15-06 |  |  | ΔU [V]
| absDynVoltageDrop | decimal | 24 | x | [6 empty] | 15-08 |  |  | ΔU_dyn [V]
InterimResults | [13 empty] | Interim Results
| LoadType | choice | 47 | x | x | [8 empty] | Type of load
[6 empty] | x | inductive |  |  |  |  | -1 |  | inductive
| NumberPoles | decimal | 50 | x | x | [8 empty] | Number of poles
[6 empty] | x | 1.7321
| phi_dyn | decimal | 23 | x | x | [5 empty] | 15-07 |  |  | ϕ_dyn [°]
| NominalVoltage | decimal | 16 | x |  | C |  | C | C |  | 10-03 |  |  | Un [V]
| R1 | decimal | 17 | x | [6 empty] | 15-01 |  |  | R1 [mΩ]
| X1 | decimal | 18 | x | [6 empty] | 15-02 |  |  | X1 [mΩ]