## Revision
Date | Description | Version | Author | Status Implementation | Status Product Knowledge | Change Valid From in ERP | Knowledge Base Version CRM
2016-03-31 | Document created | 1.0 | JR | not implemented | not released
2016-04-02 | Adding attributes | 1.1 | JR | not implemented | not released
2016-04-19 | Update attributes | 1.2 | JR | not implemented | not released
11.May.16 | Update attributes / review Omar | 1.3 | JR | not implemented | not released

## Root Material
Product |  |  | Labels
| Name | LV-SB-MF | en | MF Switchboard
productImage
| UnitofMeasure | Piece
| Optional allowed | true
| Discount allowed | true
| Export to ECC | TRUE
| Export to CRM | FALSE
| Product Status | active
| Product Type | FINISHEDGOOD
| Category | SwitchboardCategory
| KnowledgeBase Name | LV-SB-MF-KB
ERP ID
| Use BOM Entry | FALSE
Settings
| CreateProductsBOM | FALSE
SAP System
Client
Note on B16: friedrich.teucher: controls if products on tab 'BOM' are created on import

## BOM
[10 empty] | Attibutes | BB
[9 empty] | http://www.inmindcomputing.com/application/products/products-schema.owl# | http://www.inmindcomputing.com/application/products/products-schema.owl#materialCost | http://www.inmindcomputing.com/application/products/products-schema.owl#materialRoutingAssemblyHrs | http://www.inmindcomputing.com/application/products/products-schema.owl#materialRoutingBusbarTechnHrs | http://www.inmindcomputing.com/application/products/products-schema.owl#materialRoutingBasbarCellHrs | http://www.inmindcomputing.com/application/products/products-schema.owl#materialRoutingLaserHrs | http://www.inmindcomputing.com/application/products/products-schema.owl#materialRoutingWiringHrs
[10 empty] | decimal | decimal | decimal | decimal | decimal | decimal
ERPMaterialCode | CPQproductECCId | SalesBOM | CATEGORY | Product Type | Export to ECC | Export to CRM | CURRENCY | COST | KnowledgeBaseType | Costs | RoutingAssemblyHrs | RoutingBusbarTechnHrs | RoutingBasbarCellHrs | RoutingLaserHrs | RoutingWiringHrs

## Attributes
[19 empty] | Selectable if | [28 empty] | Selected if | [12 empty] | Attribution Factor | Enablement | Short Text |  | Long Text
http://www.inmindcomputing.com/application/application-schema.owl#Group |  | http://www.inmindcomputing.com/platform/platform-schema.owl#DynamicSymbolicAttribute | Type | http://www.inmindcomputing.com/platform/platform-schema.owl#dynamicAttributeMultiValued | http://www.inmindcomputing.com/platform/platform-schema.owl#dynamicAttributeMandatory | http://www.inmindcomputing.com/platform/platform-schema.owl#dynamicAttributeEnumerable | http://www.inmindcomputing.com/platform/platform-schema.owl#dynamicAttributeReadOnly | Default | http://www.inmindcomputing.com/platform/platform-schema.owl#dynamicAttributeHidden | http://www.inmindcomputing.com/application/application-schema.owl#decimalRangePrecision | http://www.inmindcomputing.com/application/application-schema.owl#decimalRangeMin, http://www.inmindcomputing.com/application/application-schema.owl#integerRangeMin | http://www.inmindcomputing.com/application/application-schema.owl#decimalRangeMax, http://www.inmindcomputing.com/application/application-schema.owl#integerRangeMax | http://www.inmindcomputing.com/application/application-schema.owl#decimalRangeSteps, http://www.inmindcomputing.com/application/application-schema.owl#integerRangeSteps | http://www.inmindcomputing.com/application/application-schema.owl#stringRangeExpression | ?? | USER | http://www.inmindcomputing.com/platform/platform-schema.owl#SymbolicValue | ComponentSelection | Selectable | [28 empty] | http://www.inmindcomputing.com/platform/platform-schema.owl#selectsSymbolicValue | [12 empty] | http://www.inmindcomputing.com/application/application-schema.owl#attributionFactor\ | http://www.inmindcomputing.com/application/application-implementation.owl# | http://www.w3.org/2000/01/rdf-schema#label |  | http://www.w3.org/2000/01/rdf-schema#comment
Group ID | Sub Group ID | Characteristic ID | Type | MultiValued | Input Mandatory | enumerable | Read Only | Default | Hidden | Precision | Min | Max | Steps | String Range | DomainFromTable | Values | Value ID | Component Selection | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selectable if | Selected if | Selected if | Selected if | Selected if | Selected if | Selected if | Selected if | Selected if | Selected if | Selected if | Selected if | Selected if | Selected if |  | SalesOrg | en | pt | en | pt
Group_Electrical_Details | [62 empty] | Electrical Details
| SwitchboardMFGroup | [61 empty] | Switchboard MF
|  | LV-SB-MF_VOLTAGE | choice |  | x | x | [56 empty] | Rated operating voltage (Ue)
[8 empty] | x | [7 empty] | SB_Operating_Voltage_400 | SB_Operating_Voltage_400 | [45 empty] | 400 Vac
[16 empty] | SB_Operating_Voltage_380 | SB_Operating_Voltage_380 | [45 empty] | 380 Vac
[16 empty] | SB_Operating_Voltage_220 | SB_Operating_Voltage_220 | [45 empty] | 220 Vac
|  | LV-SB-MF_FREQUENCY | choice |  | x | x | [56 empty] | Rated frequency
[16 empty] | SB_FREQUENCY_50HZ | SB_FREQUENCY_50HZ | [45 empty] | 50 HZ
[8 empty] | x | [7 empty] | SB_FREQUENCY_60HZ | SB_FREQUENCY_60HZ | [45 empty] | 60 HZ
|  | LV-SB-MF_IBB | choice |  | x | x | [56 empty] | Main busbars rated current (Ie) [A]
[16 empty] | SB_BUSBAR_RATING_6300 | SB_BUSBAR_RATING_6300 | [45 empty] | 6300
[16 empty] | SB_BUSBAR_RATING_5000 | SB_BUSBAR_RATING_5000 | [45 empty] | 5000
[8 empty] | x | [7 empty] | SB_BUSBAR_RATING_4000 | SB_BUSBAR_RATING_4000 | [45 empty] | 4000
[16 empty] | SB_BUSBAR_RATING_3200 | SB_BUSBAR_RATING_3200 | [45 empty] | 3200
[16 empty] | SB_BUSBAR_RATING_3000 | SB_BUSBAR_RATING_3000 | [45 empty] | 3000
[16 empty] | SB_BUSBAR_RATING_2500 | SB_BUSBAR_RATING_2500 | [45 empty] | 2500
[16 empty] | SB_BUSBAR_RATING_2000 | SB_BUSBAR_RATING_2000 | [45 empty] | 2000
[16 empty] | SB_BUSBAR_RATING_1600 | SB_BUSBAR_RATING_1600 | [45 empty] | 1600
[16 empty] | SB_BUSBAR_RATING_1250 | SB_BUSBAR_RATING_1250 | [45 empty] | 1250
[16 empty] | SB_BUSBAR_RATING_1000 | SB_BUSBAR_RATING_1000 | [45 empty] | 1000
|  | LV-SB-MF_BBSYSTEM | choice |  | x | x | [56 empty] | Main busbars system
[8 empty] | x | [7 empty] | SB_BUSBAR_SYSTEM_3P+N+PE | SB_BUSBAR_SYSTEM_3P+N+PE | [45 empty] | 3P+N+PE
[16 empty] | SB_BUSBAR_SYSTEM_3P+PEN | SB_BUSBAR_SYSTEM_3P+PEN | [45 empty] | 3P+PEN
[16 empty] | SB_BUSBAR_SYSTEM_4P+PE | SB_BUSBAR_SYSTEM_4P+PE | [45 empty] | 4P+PE
|  | LV-SB-MF_ICW | choice |  | x | x | [56 empty] | MBB rated short-time withstand current (Icw)
[16 empty] | SB_ICW_50 | SB_ICW_50 | [45 empty] | 50 kA
[16 empty] | SB_ICW_65 | SB_ICW_65 | [45 empty] | 65 kA
[16 empty] | SB_ICW_85 | SB_ICW_85 | [45 empty] | 85 kA
[8 empty] | x | [7 empty] | SB_ICW_100 | SB_ICW_100 | [45 empty] | 100 kA
[16 empty] | SB_ICW_120 | SB_ICW_120 | [45 empty] | 120 kA
|  | LV-SB-MF_PANEL_ACCESS | choice |  | x | x | [56 empty] | Panel access
[8 empty] | x | [7 empty] | SB_PANEL_ACCESS_FRONT | SB_PANEL_ACCESS_FRONT | [45 empty] | Front
[16 empty] | SB_PANEL_ACCESS_REAR | SB_PANEL_ACCESS_REAR | [45 empty] | Rear
[16 empty] | SB_PANEL_ACCESS_SIDE | SB_PANEL_ACCESS_SIDE | [45 empty] | Side
|  | LV-SB-MF_CONTROL_VOLTAGE | choice |  | x | x | [56 empty] | Control voltage (Uc)
[8 empty] | x | [7 empty] | SB_CONTROL_VOLTAGE_NO | SB_CONTROL_VOLTAGE_NO | [45 empty] | No
[16 empty] | SB_CONTROL_VOLTAGE_110 | SB_CONTROL_VOLTAGE_110 | [45 empty] | 110 Vac
[16 empty] | SB_CONTROL_VOLTAGE_220 | SB_CONTROL_VOLTAGE_220 | [45 empty] | 220 Vac
|  | LV-SB-MF_SEISMIC | choice |  |  | x | [56 empty] | Withstand for seismic up to Richter scale-8
[8 empty] | x | [7 empty] | SB_SEISMIC_N | SB_SEISMIC_N | [45 empty] | No
[16 empty] | SB_SEISMIC_Y | SB_SEISMIC_Y | [45 empty] | Yes
|  | LV-SB-MF_ARC | choice |  |  | x | [56 empty] | Internal arc fault proof
[8 empty] | x | [7 empty] | SB_ARC_N | SB_ARC_N | [45 empty] | No
[16 empty] | SB_ARC_Y | SB_ARC_Y | [45 empty] | Yes
|  | LV-SB-MF_POLE | choice |  |  | x | [56 empty] | Breaker Poles (Default)
[8 empty] | x | [7 empty] | SB_3POLE | SB_3POLE | [45 empty] | 3 Pole
[16 empty] | SB_4POLE | SB_4POLE | [45 empty] | 4 Pole
|  | LV-SB-MF_RUD | choice |  |  | x | [56 empty] | R&D Status
[16 empty] | SB_RUD_STANDARD | SB_RUD_STANDARD |  | SB_BUSBAR_RATING_4000 | SB_BUSBAR_RATING_3200 | SB_BUSBAR_RATING_3000 | SB_BUSBAR_RATING_2500 | SB_BUSBAR_RATING_2000 | SB_BUSBAR_RATING_1600 | SB_BUSBAR_RATING_1250 | SB_BUSBAR_RATING_1000 | [36 empty] | Standard
[16 empty] | SB_RUD_CONSTRUCT | SB_RUD_CONSTRUCT |  | SB_BUSBAR_RATING_5000 | SB_BUSBAR_RATING_6300 | [42 empty] | Development
| SubGroup_Mechanical_Details_for_Enclosure | [61 empty] | Mechanical Details for Enclosure
|  | LV-SB-MF_SEPERATION | choice |  | x | x | [56 empty] | Forms of separation
[16 empty] | SB_FORM_1 | SB_FORM_1 | [45 empty] | Form1
[16 empty] | SB_FORM_2 | SB_FORM_2 | [45 empty] | Form2
[16 empty] | SB_FORM_3 | SB_FORM_3 | [45 empty] | Form3
[8 empty] | x | [7 empty] | SB_FORM_4 | SB_FORM_4 | [45 empty] | Form4
|  | LV-SB-MF_THICKENS | choice |  | x | x | [56 empty] | Thickness of Enclosure / Frams [mm]
[8 empty] | x | [7 empty] | SB_1-6_2-0-MM | SB_1-6_2-0-MM | [45 empty] | 1.6mm Sheet/2.0mm Frame
[16 empty] | SB_2-0_2-0-MM | SB_2-0_2-0-MM | [45 empty] | 2.0mm Sheet/2.0mm Frame
|  | LV-SB-MF_IP | choice |  | x | x | [56 empty] | Degrees of protection up to
[8 empty] | x | [7 empty] | SB_IP42 | SB_IP42 | [45 empty] | IP 42
[16 empty] | SB_IP54 | SB_IP54 | [45 empty] | IP 54
|  | LV-SB-MF_DEPTH | decimal |  | x | x | [56 empty] | Depth of panel [mm]
[16 empty] | 600 | 600
[8 empty] | x | [7 empty] | 800 | 800
[16 empty] | 1000 | 1000
|  | LV-SB-MF_VENTILATION | choice |  | x | x | [56 empty] | Forced Ventilation
[8 empty] | x | [7 empty] | SB_VENTILATION_NATURAL | SB_VENTILATION_NATURAL | [45 empty] | No
[16 empty] | SB_VENTILATION_FORCED | SB_VENTILATION_FORCED | [45 empty] | Yes
|  | LV-SB-MF_COLOR | choice |  | x | x | [56 empty] | Paint finish
[8 empty] | x | [7 empty] | SB_COLOR_STANDARD | SB_COLOR_STANDARD | [45 empty] | RAL7035 (light grey)
[16 empty] | SB_COLOR_CUSTOM | SB_COLOR_CUSTOM | [45 empty] | Custom
|  | LV-SB-MF_BASE_HEIGHT | decimal |  | x | x | [56 empty] | SKD base Height [mm]
[8 empty] | x | [7 empty] | 50 | 50
[16 empty] | 100 | 100
[16 empty] | 150 | 150
[16 empty] | 200 | 200
|  | LV-SB-MF_HEIGHT | char |  |  |  | x | [55 empty] | Height over base [mm]
[8 empty] | x | [7 empty] | 2150 | 2150 | [45 empty] | 2150
| SubGroup_Busbars_Details | [61 empty] | Busbars Details
|  | LV-SB-MF_INCOM_CABLE | choice |  | x | x | [56 empty] | Incoming cable entry
[8 empty] | x | [7 empty] | SB_INCOM_CABLE_BOTTOM | SB_INCOM_CABLE_BOTTOM | [45 empty] | Bottom
[16 empty] | SB_INCOM_CABLE_TOP | SB_INCOM_CABLE_TOP | [45 empty] | Top
|  | LV-SB-MF_OUT_CABLE | choice |  |  | x | [56 empty] | Outgoing cable
[16 empty] | SB_INCOM_OUT_BOTTOM | SB_INCOM_OUT_BOTTOM | [30 empty] | SB_INCOM_CABLE_BOTTOM | [14 empty] | Bottom
[16 empty] | SB_INCOM_OUT_TOP | SB_INCOM_OUT_TOP | [30 empty] | SB_INCOM_CABLE_TOP | [14 empty] | Top
|  | LV-SB-MF_BBP | choice |  | x | x | [56 empty] | Main busbars position
[16 empty] | SB_LHBB | SB_LHBB | [30 empty] | SB_INCOM_CABLE_TOP | [14 empty] | Lower Horizontal Busbar
[16 empty] | SB_UHBB | SB_UHBB | [30 empty] | SB_INCOM_CABLE_BOTTOM | [14 empty] | Upper Horizontal Busbar
|  | LV-SB-MF_BB_SLEEVE | choice |  | x | x | [56 empty] | Busbar sleeving
[8 empty] | x | [7 empty] | SB_BB_SLEEVING_NO | SB_BB_SLEEVING_NO | [45 empty] | No
[16 empty] | SB_BB_SLEEVING_YES | SB_BB_SLEEVING_YES | [45 empty] | Yes
|  | LV-SB-MF_BB_PLATING | choice |  | x | x | [56 empty] | Busbar plating
[8 empty] | x | [7 empty] | SB_BB_NO | SB_BB_NO | [45 empty] | Bare
[16 empty] | SB_BB_TIN | SB_BB_TIN | [45 empty] | Tin
[16 empty] | SB_BB_SILVER | SB_BB_SILVER | [45 empty] | Silver
|  | LV-SB-MF_BB-CROSS-SECTION | choice |  | x | x | [56 empty] | Busbar Size [ n x mm x mm]
[16 empty] | SB_BUSBAR_SIZE_1x85x10 | SB_BUSBAR_SIZE_1x85x10 |  |  | SB_BUSBAR_RATING_1250 | [27 empty] | SB_BUSBAR_RATING_1000 | [14 empty] | 1 x 85 x 10
[16 empty] | SB_BUSBAR_SIZE_2x55x10 | SB_BUSBAR_SIZE_2x55x10 | [30 empty] | SB_BUSBAR_RATING_1600 | [14 empty] | 2 x 55x 10
[16 empty] | SB_BUSBAR_SIZE_2x70x10 | SB_BUSBAR_SIZE_2x70x10 | [30 empty] | SB_BUSBAR_RATING_2000 | [14 empty] | 2 x 70 x 10
[16 empty] | SB_BUSBAR_SIZE_2x85x10 | SB_BUSBAR_SIZE_2x85x10 | [30 empty] | SB_BUSBAR_RATING_2500 | [14 empty] | 2 x 85 x 10
[16 empty] | SB_BUSBAR_SIZE_3x100x10 | SB_BUSBAR_SIZE_3x100x10 |  |  | SB_BUSBAR_RATING_3200 | [27 empty] | SB_BUSBAR_RATING_3000 | [14 empty] | 3 x 100 x 10
[8 empty] | x | [7 empty] | SB_BUSBAR_SIZE_4x100x10 | SB_BUSBAR_SIZE_4x100x10 | [30 empty] | SB_BUSBAR_RATING_4000 | [14 empty] | 4 x 100 x 10
[16 empty] | SB_BUSBAR_SIZE_4x150x10 | SB_BUSBAR_SIZE_4x150x10 |  |  | SB_BUSBAR_RATING_6300 | [27 empty] | SB_BUSBAR_RATING_5000 | [14 empty] | 4 x 150 x 10
|  | LV-SB-MF_BB_N_SIZE | choice |  | x | x | [56 empty] | Neutral busbars size
[16 empty] | SB_BB_N_50P | SB_BB_N_50P | [45 empty] | 50% from main busbar
[8 empty] | x | [7 empty] | SB_BB_N_100P | SB_BB_N_100P | [45 empty] | 100% from main busbar
|  | LV-SB-MF_BB_PE_SIZE | choice |  | x | x | [56 empty] | Earth busbars size
[8 empty] | x | [7 empty] | SB_BB_PE_25P | SB_BB_PE_25P | [45 empty] | 25% from main busbar
[16 empty] | SB_BB_PE_50P | SB_BB_PE_50P | [45 empty] | 50% from main busbar
[16 empty] | SB_BB_PE_100P | SB_BB_PE_100P | [45 empty] | 100% from main busbar
|  | LV-SB-MF_CABLE_SIZE | choice |  |  | x | [56 empty] | Cable size
[8 empty] | x | [7 empty] | SB_CABLE_SIZE_STD | SB_CABLE_SIZE_STD | [45 empty] | As per our standard
[16 empty] | SB_CABLE_SIZE_NO_STD | SB_CABLE_SIZE_NO_STD | [45 empty] | Not as per our standard
Note on S84: YYS: readonly , for information

## types (hidden)
data types | boolean
choice
boolean
numeric

## ERP Org (hidden)
Sales Org |  |  | Distribution Channel |  |  |  | Plant
0001 | SL Wetzlar | 0001 SL Wetzlar | 01 | Wz:BO Maschinen | Wz:Opht.Opt.Machines | 01 Wz:Opht.Opt.Machines | 0001 | Satisloh GmbH Brillenoptik | 0001 Satisloh GmbH Brillenoptik
0002 | LOH Oensingen | 0002 LOH Oensingen | 02 | Wz:Consumables | Wz:Consumables | 02 Wz:Consumables | 0002 | Satisloh Oensingen AG-obsolet | 0002 Satisloh Oensingen AG-obsolet
0003 | SL Baar | 0003 SL Baar | 03 | Wz:BO Dienstleistung | Wz:Opht.Opt.Services | 03 Wz:Opht.Opt.Services | 0003 | Satisloh AG | 0003 Satisloh AG
0004 | SL France | 0004 SL France | 04 | LOH Oensingen | LOH Oensingen | 04 LOH Oensingen | 0004 | Satisloh France S.A.S. | 0004 Satisloh France S.A.S.
0005 | SL USA | 0005 SL USA | 11 | Wz:FO Dienstleistung | Wz:Prec.Opt.Services | 11 Wz:Prec.Opt.Services | 0005 | Satisloh North America Inc. | 0005 Satisloh North America Inc.
0006 | SL Hongkong | 0006 SL Hongkong | 12 | Wz:FO Maschinen | Wz:Prec.Opt.Machines | 12 Wz:Prec.Opt.Machines | 0006 | Satisloh Asia Ltd. | 0006 Satisloh Asia Ltd.
0007 | SL Zhongshan | 0007 SL Zhongshan | 18 | SL Danyang | SL Danyang | 18 SL Danyang | 0007 | Satisloh Zhongshan | 0007 Satisloh Zhongshan
0008 | SL Settimo | 0008 SL Settimo | 30 | SL Baar | SL Baar | 30 SL Baar | 0008 | Satisloh Italy S.r.l. | 0008 Satisloh Italy S.r.l.
0009 | SL Horgen | 0009 SL Horgen | 40 | SL France | SL France | 40 SL France | 0009 | Satisloh Photonics AG | 0009 Satisloh Photonics AG
0018 | SL Danyang | 0018 SL Danyang | 50 | SL USA | SL USA | 50 SL USA | 0011 | Satisloh GmbH Feinoptik | 0011 Satisloh GmbH Feinoptik
|  |  | 60 | SL Hongkong | SL Hongkong | 60 SL Hongkong | 0018 | Satisloh Danyang | 0018 Satisloh Danyang
|  |  | 70 | SL Zhongshan | SL Zhongshan | 70 SL Zhongshan | 001S | SL GmbH Spain | 001S SL GmbH Spain
|  |  | 80 | SL Settimo | SL Settimo | 80 SL Settimo | 005C | Satisloh Warehouse Canada | 005C Satisloh Warehouse Canada
|  |  | 90 | SL Horgen | SL Horgen | 90 SL Horgen